## Slide 1: Measurement and Modelling of Ice Rink Heat Loads
Mazyar Karampour, mazyar@kth.se, TSUEM
Supervisor: Dr.Joachim Claesson, joachim.claesson@energy.kth.se
KTH, Energy Technology Department
Rapport available at: http://kth.diva-portal.org/smash/record.jsf?pid=diva2:478941

## Slide 2: Introduction: Energy Consumption in Ice Rinks
Chart: 
| Refrigeration | Heating | Lighting | Ventilation Fans | Dehumidification | Miscellaneous | Misc. Pumps
 | 43 | 26 | 10 | 9 | 6 | 5 | 1
Chart: 
| Compressors | Brine Pumps | Coolant Pumps | Dry Cooler Fans
 | 80 | 10 | 5 | 5
More than 350 indoor ice rinks
More than 300 Gwh annual energy consumption
The biggest consumer: Refrigeration System
Solution: less Heat Loads on the Refrigeration System

## Slide 3: Method: Refrigeration & Heat Loads Analysis
Condensation
Convection
Lighting
Radiation
Ice resurfacing
Skaters
Ground conduction
Brine headers
Brine pump
Ice
Evaporator
Concrete
Insulation
NH3
NH3
Brine
Evaluation the Performance of Refrigeration by ClimaCheck Measurements
Heat Load Calculations based on Heat Transfer Correlations and Field Measurements
1
2

## Slide 4: Results: Energy Consumption &Heat Load shares
Chart: 
| radiation | lighting | convection+condensation | ice resurfacing | header pipe | brine pump | ground | skaters
 | 792 | 234 | 1236 | 486 | 160.8 | 216 | 168 | 137.2
Chart: Energy consumption (Kwh/day)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Älta consumption (kWh/day) | 1448 | 1539 | 1557 | 1515 | 1552 | 1551 | 1517 | 1542 | 1544 | 1589 | 1513 | 1580 | 1583 | 1540 | 1559 | 1512 | 1493 | 1508 | 1616 | 1620 | 1609 | 1662 | 1538 | 1521 | 1530 | 1564 | 1541 | 1592 | 1518 | 1537 | 1552
Norrtälje consumption (kWh/day) | 811 | 832 | 987 | 808 | 792 | 789 | 932 | 926 | 864 | 1033 | 847 | 941 | 860 | 793 | 714 | 733 | 977 | 1105 | 1172 | 942 | 922 | 967 | 985 | 1032 | 944 | 946 | 852 | 890 | 1010 | 965 | 1046
Älta temp. | -2.21 | -1.54 | -0.75 | 0.13 | 1.2 | -2.26 | -1.27 | 2.51 | 1.25 | 2.21 | 1.64 | 3.28 | 0.52 | 1.33 | -0.08 | -2.52 | -1.01 | 0.2 | 1.01 | 1.88 | 4.45 | 8.34 | 6.35 | 3.64 | 0.9 | -0.57 | 0.96 | 1.54 | 0.23 | 0.54 | 1.25
Norrtälje temp. | -1.92 | -0.14 | 1.18 | 1.62 | 2.25 | -0.49 | 0.16 | 3.04 | 2.07 | 2.78 | 1.89 | 3.98 | 2.53 | 1.88 | -0.85 | -1.03 | -0.35 | 0.81 | 2.83 | 3.88 | 4.73 | 8.35 | 6.9 | 4.18 | 0.38 | 0.95 | 2.34 | 2.38 | 1.21 | 1.1 | 0.48