## Slide 1: Nuclear Fuel Cycle 2013
Lecture 7: Reactor Chemistry

## Slide 2: Water Chemistry
WATER CHEMISTRY
FUEL
MATERIAL
RADIATION
WASTE
CLEANING SYSTEMS
DEGASSING
DECONTAMINATION
Corrosion  aging of power plant
Big deposits on fuel  decrease cooling, damage encapsulation, lower reactivity
Water chemistry, corrosion and material interact giving radioactive contamination

## Slide 3: Water Chemistry, 25°C
δ-
δ+
104.45°
Hydrogen bonds between molecules  high boiling point
Angle between H-O-H  high dipole moment  great solvent for salts
1.8Å
1.0Å
Addition of acid increases conductivity greatly since H+ can easily “jump” through the structure (and so can OH-)

## Slide 4: Water Chemistry, 300°C
High thermal movement
Most H-bonds broken
lower viscosity
Lower steam pressure
Harder for dipoles to align in electric fields
Less polar solvent; more like benzene
lower solubility for salts
Kw=[H3O+][OH-]~2×10-11 M2
Neutral pH=5.65
11
12
13
14
15
0
100
200
300
Temperature, °C
-LOG Kw

## Slide 5: Surface tension

## Slide 6: Viscosity

## Slide 7: Solubility of gases
Henry’s law:
p = kH c
p = Partial pressure of gas
kH = Henry’s constant (temperature dependent)
c = concentration of gas in solution
O2
H2
Solubility of H2, O2, N2 more than twice as high at 300 °C

## Slide 8: Density

## Slide 9: Conductivity
Dependent on concentration and mobility of ions
κ = 10-3 Σλi ci
κ = conductivity [S/cm]
λi = equivalent conductivity for ion i [cm2·S·mol-1]
ci = concentration of ion i [mol·l-1 ]
λ high for H+ and OH-
Pure water κ = 0.054 µS
Feeding water κ = 0.1 µS
Reactor water κ = 0.1-0.3 µS
Tap water κ = 100-300 µS

## Slide 10: Ion exchangers
To remove undesired ions from the waters of a nuclear power plant, ion exchangers are used
Organic
Polymeric resins
Usually polystyrene with functional groups Cross-binding with divinylbenzene
Functional group cation exchanger (sulphonic acid)
Functional group anion exchanger (quartinary ammonium)

## Slide 11: Radiation chemistry
The radiation field in a reactor is of course very strong
γ-radiation and neutrons will cause water radiolysis

## Slide 12: Water Radiolysis
H2O
H2O×
H2O+ + e-
Event
Time scale
10-16 s
•OH + H3O+
10-14 s
H2O
H• + •OH
H2+•O
10-13 s
Formation of molecular products in the spurs and diffusion of radicals out of the spurs
eaq-, H•, •OH, H2, H2O2, H3O+
10-7 s

## Slide 13: Radical reactions following water radiolysis
OH· + H2  H· + H2O k= 4.0×107 OH· + H2O2  HO2· + H2Ok= 2.25×107
OH· + O2-·  O2 + OH- k= 1.0×1010 H· + O2  H+ + O2-· k= 2.0×1010
H· + O2-·  HO2- k= 2.0×1010 eaq-· + O2  O2-· k= 2.0×1010
eaq-· + H2O2  OH· + OH- k= 1.6×1010 eaq-· + O2-·  HO2- + OH- k= 1.2×1010
eaq-· + H+  H· k= 2.2×1010 eaq-· + H2O  H· + OH- k= 2.0×101
eaq-· + HO2-  O-· + OH- k= 3.5×109 OH· + HO2·  H2O + O2 k= 1.2×1010
OH· + OH·  H2O2 k= 4.0×109 H· + HO2·  H2O2 k= 2.0×1010
H· + H2O2  H2O + OH· k= 6.0×107 H· + OH-  eaq-· + H2O k= 2.0×107
HO2· + O2-·  O2 + HO2- k= 8.5×107 HO2· + HO2·  H2O2 + O2 k= 7.5×105
H+ + O2-·  HO2· k= 5.0×1010 HO2·  H+ + O2-· k= 8.0×105
H+ + HO2-  H2O2 k= 2.0×1010 H2O2  H+ + HO2- k= 3.56×10-2
OH· + OH-  H2O + O-· k= 1.2×1010 O-· + H2O  OH· + OH- k= 1.7×106
H+ + OH-  H2O k= 1.43×1011 H2O  H+ + OH- k= 2.6×10-5
H· + OH·  H2O k= 2.5×1010 H· + H·  H2 k= 1.0×1010
eaq-· + H·  H2 + OH- k= 2.0×1010 eaq-· + eaq-·  H2 + OH- + OH- k= 5.0×109
eaq-· + OH·  OH- k= 2.0×1010 O-· + H2  H· + OH- k= 8.0×107
O-· + H2O2  H2O + O2-· k= 2.0×108 OH· + HO2-  HO2· + OH- k= 5.0×109
HO2- + O-·  OH- + O2-· k= 8.0×108 eaq-· + O2-·  HO2- + OH- k= 2.0×1010
OH- + H2O2  HO2- + H2O k= 5.0×108 HO2- + H2O  H2O2 + OH- k= 5.735×104

## Slide 14: Radiation chemistry
H2O2, O2 and H2 are the molecular products formed from water radiolysis
The system will reach steady state concentrations of radicals
The steady state concentrations can easily change when other species are added to the system
O2 is not desired in the reactor water of a PWR. The reactor water contains H3BO3 and LiOH. The conductivity is high and O2 could corrode materials in the reactor. The O2 concentration is kept <1 ppb by adding H2 to reactor water (no continuous addition is required)

## Slide 15: BWR water chemistry
- Addition of H2 to avoid risk of intercrystalline stress corrosion of the construction materials of the reactor. (AWC/HWC)
Traditionally two “schools” to control water chemistry
- No additions. Instead highest possible purity (NWC)

## Slide 16: Sources of impurities
- Radiolysis of the coolant (radicals, H2, O2, H2O2)
- Corrosion and erosion of construction material of turbine and reactor systems (metal ions)
- Activation of impurities that have deposited on the fuel encapsulation (radioactive nuclides in the system)
- Radiolysis of the coolant (radicals, H2, O2, H2O2)
- Introduction of impurities by dilution water
Temporary introduction of impurities. For instance
  Fission products from damaged fuel.
  Seepage of filter and ion exchange material
  Seepage of seawater through damaged turbines

## Slide 17: Corrosion products
Corrosion products are the impurities that are present in the highest concentrations
Originates from erosion and corrosion of construction materials of the turbine and reactor systems
Most often deposit on the reactor core
Increased hydraulic resistance
> increased pressure drop over the core
- Heat resistance in deposit decreases heat conduction between fuel and coolant
- Reactivity loss due to increased fuel temperature and neutron absorption in deposit
Formation and spreading of activated corrosion products -> main source to dose to personnel

## Slide 18: Organic substances
Humic substances
Bacteria
Leakage of synthetic organic substances (ion exchangers, cleaners, oils, etc.)
Humic substances: Originates from leakage when desalinating water
Causes operation problem; corrosion, lowering efficiency of filters, can adsorb irreversibly to ion exchangers
Bacteria: can grow in almost any system, best 0-80°C and access to carbon
Exchange resin: Relatively common. Decomposes at higher temperatures, gives nitrate and sulfate in reactor water

## Slide 19: PWR water chemistry
- Control the corrosion of the construction material (H2(aq), Zn)
The goals for the water treatment:
- Control the reactivity of the fuel (Boric acid; H3BO3)
- Contribute to lower the radiation levels
- pH control (LiOH)

## Slide 20: Activated corrosion products
CRUD: “Chalk River Unidentified Deposit”
Radioactive deposits in reactor systems
The main part of doses to personnel originates from activated corrosion products.
60Co worst. Gives 2/3 of dose to personnel
~75% of the dose to personnel is given at maintenance work (during outage)

## Slide 21: Actions
Low Co-supply: Minimize the usage of Co in construction material
Lower the rate of deposit release from fuel (force deposits to stay on fuel)
More efficient water purification. Send larger part of reactor water through purification system.
Lower tendency to deposit on surfaces in reactor system. Smoother surfaces, avoid pockets where crud can accumulate (add Zn)

## Slide 22: Decontamination
Removal of CRUD/Decontamination:
Non chemical methods
Chemical methods
Electrochemical methods

## Slide 23: High pressure water jet cleaning
+ Fast
+ Good decontamination results
+ Water is compatible with most materials
- Produces big volumes of waste
- Blasting units might become jammed

## Slide 24: Mechanical decontamination
+ Fast
+ Well established
+ Automation possible
- Destructive
- High particle production
- Waste

## Slide 25: Chemical decontamination
+ Good contamination results
+ Small waste volumes
+ Can contaminate small to large systems
+ Can contaminate complex geometries
- Time consuming (oxidation, reduction, removal in cycles)
- Complex assembling/disassembling
- Material incompatibility

## Slide 26: Electrochemical decontamination
+ Fast
+ Good contamination results
+ Smoothens the surface on the base material, preventing recontamination
- Does not work with tight oxide layers
- Expensive
- Complex construction

## Slide 27: Activation of coolant
Activation of oxygen: Gives short-lived nuclides 15C (t½=2.45s, Eγ=5.3MeV) and 16N (t½=7.13s, Eγ=6MeV)
N-16 dominating radiation source in water and steam
In reactor systems where H2 is added NH3 will form which increases activity in steam
Other coolant activation products: O-19, F-18. N-13 and H-3

## Slide 28: Corrosion
Galvanic corrosion
Pitting corrosion
Local corrosion
Erosion corrosion
Stress corrosion

## Slide 29: Erosion Corrosion
Local corrosion
Also mechanic part. Shear stress tears off corrosion products
Occurs in streaming systems. The higher the flow, the thinner the diffusion layer at the surface of the metal
-> supply of corroding agents and removal of corrosion products faster
Choose low alloy steel
(add oxygen; gives some protection to erosion)

## Slide 30: Stress Corrosion
Alkaline transgranular stress corrosion (TGSCC): Tension in combination with high OH- concentrations. Occurs in gaps and crevices where concentration can increase
Intergranular or transgranular corrosion:
progress along grain boundaries or not
Intergranular stress corrosion (IGSCC): Biggest material problem for BWR.
Occurs close to weldings and austenitic stainless steel
Tension, sensibilized material and oxidizing conditions are needed
Remove one of these condition to prevent corrosion.

## Slide 31: Influence of added elements
Addition of Cl-: Accelerates IGSCC
Addition of SO42-: Accelerates IGSCC. Accumulates in oxide films giving long term effects
Addition of Cu2+: Accelerates IGSCC. Synergic effect together with Cl-.
Addition of NO3-: Does not increase risk of IGSCC, can have positive effects
Addition of Si: Small increased risk of IGSCC at c>500 ppb
Addition of CO2: Small effect on IGSCC

## Slide 32: Water purification
BWR work with very pure water
Most important water purification systems: Condensate purification system and Reactor water purification
Mainly: Filtration (of mainly FeOOH) in Condensate purification Ion exchange in Reactor water purification

## Slide 33: Water purification
PWR more complex since boric acid and LiOH are added
Control concentration of boric acid, H2 and LiOH in reactor water
Control water level in pressure vessel
Remove corrosion and fission products from reactor water